## Slide 1
KJEI’s, Trinity Academy of Engineering
Department of Electronics and
Telecommunication Engineering
Academic Year 2026–27 Semester I
Project Review 3
    Under the guidance of
Prof. Chetna Jain
Date: 3 October 2026
WattSense
Battery Monitoring and Priority Load Control
Students
Dhanesh Chaudhari
Yash Ahire
Mrudula Pagar
Ujjwal Kshirsagar
Roll No.
4114
4101
4114
4101
Notes: WattSense studies battery monitoring and priority control for a small DC system. The Review 3 evidence covers a software prototype, a routed PCB and simulations. Physical assembly is the next stage.
Sources
User-supplied author/department/date details, 1 October 2026. College identity and logos retained from supplied template.

## Slide 2
Introduction and Topic Overview
A battery powers a 5 V lamp and an optional fan through a converter.
Keeping both loads on can shorten the service available to the lamp.
WattSense estimates remaining charge and sheds the fan when backup becomes limited.
A purchased BMS protects the cells. Our board measures current and controls load priority.
Intended use: a small DC backup demonstrator for lighting and ventilation.
Review 3 status: software, PCB design and simulation evidence.
Hardware measurements and solar tests remain pending.
Notes: The design uses a protected 4S LiFePO4 pack, a matched charger, an external converter and an ESP32. Only the fan return is switched. Solar hardware is an extension after the battery-only demonstration. Do not describe the dashboard as a measured prototype.
Sources
hardware/REFERENCE_WIRING.md
docs/PROJECT_FLOW.md
docs/RECHECK_2026-09-30.md

## Slide 3
Literature Survey 1 of 4
No | Author, Year | Problem | Method | Data / tests | Finding | Scope limit
1 | Marahatta et al. 2021 | Limited rural energy supply | Priority switching + SCADA | Laboratory solar-battery microgrid | Maintains essential-load service | Three-level solar system
2 | Rajbhandari et al. 2024 | Variable solar energy availability | Day-ahead forecasts + PSO | Stochastic generation/load simulations | Improves priority-load continuity | Requires forecasts and optimisation
3 | Bai et al. 2020 | Power imbalance and load priorities | Rule control + MILP shedding | Simulink day-long model | Balances power across operating modes | Converter efficiency omitted
4 | Lv et al. 2021 | Battery imbalance and bus fluctuations | Adaptive droop + SOC modes | Simulink with two stores | Balances SOC and bus power | 450 V simulated microgrid
5 | Guo & Kors 2021 | Renewable energy teaching | Sensors, Raspberry Pi, SCADA | Outdoor rig + student tests | Demonstrates integrated teaching platform | No load-runtime comparison
Notes: These studies motivate our design choices. Scope limits describe applicability to this project unless explicitly attributed to the authors. WattSense does not claim to outperform these methods.
[1] A. Marahatta, Y. Rajbhandari, A. Shrestha, A. Singh, A. Gachhadar, and A. Thapa, 'Priority-based low voltage DC microgrid system for rural electrification,' Energy Reports, vol. 7, pp. 43-51, 2021, doi: 10.1016/j.egyr.2020.11.030.
https://www.sciencedirect.com/science/article/pii/S2352484720314554
Evidence: Publisher explicitly describes experimental analysis and a low-cost SCADA implementation. Saved evidence identifies three load priorities and battery thresholds. This is close prior art, so priority shedding itself is not a new WattSense algorithm. The row states a qualitative study finding and transfers no performance percentage.
[2] Y. Rajbhandari, A. Marahatta, A. Shrestha, A. Gachhadar, A. Thapa, F. Gonzalez-Longatt, and P. Korba, 'Enhanced demand side management for solar-based isolated microgrid system: Load prioritisation and energy optimisation,' IET Smart Grid, vol. 7, no. 3, pp. 294-313, 2024, doi: 10.1049/stg2.12151.
https://ietresearch.onlinelibrary.wiley.com/doi/10.1049/stg2.12151
Evidence: Section 4 explicitly identifies simulation of stochastic load/generation conditions and three priority levels. The mechanism optimises battery SOC shedding points with PSO and forecasts. Cite issue year 2024, not online-first date December 2023. WattSense implements neither forecasting nor PSO; the comparison is scope, not superiority.
[3] W. Bai, M. Sechilariu, and F. Locment, 'DC Microgrid System Modeling and Simulation Based on a Specific Algorithm for Grid-Connected and Islanded Modes with Real-Time Demand-Side Management Optimization,' Applied Sciences, vol. 10, no. 7, Art. 2544, 2020, doi: 10.3390/app10072544.
https://www.mdpi.com/2076-3417/10/7/2544
Evidence: The full PDF was opened. The model includes PV, battery, supercapacitor, diesel and grid connection. Section 2.6 names knapsack/MILP with IBM CPLEX; section 2 explicitly omits converter efficiency. Results are simulation, not a laboratory trial. That omission is a stated author modeling choice rather than our invented criticism.
[4] J. Lv, X. Wang, G. Wang, and Y. Song, 'Research on Control Strategy of Isolated DC Microgrid Based on SOC of Energy Storage System,' Electronics, vol. 10, no. 7, Art. 834, 2021, doi: 10.3390/electronics10070834.
https://www.mdpi.com/2079-9292/10/7/834
Evidence: The publisher page direct open returned 429 but primary full text was retrieved through search, including tables and result sections. The paper uses two energy-storage units, SOC-dependent droop, and secondary-load shedding when SOC is low and generation insufficient. Its Table 2 has a 450 V bus. The simulation scope differs from the 12.8 V one-pack WattSense demonstrator.
[5] L. Guo and J. Kors, Jr., 'Design of a Laboratory Scale Solar Microgrid Cyber-Physical System for Education,' Electronics, vol. 10, no. 13, Art. 1562, 2021, doi: 10.3390/electronics10131562.
https://www.mdpi.com/2079-9292/10/13/1562
Evidence: The reported platform has a solar panel, purchased MPPT controller, rechargeable battery, relay-controlled LEDs and a toy-car charger. Hardware data were sampled every ten minutes during the reported outdoor run; do not imply WattSense data exist. The applicability limit is our scope comparison: its focus is education and integration rather than WattSense's battery-only retained-lamp comparison.
Sources

## Slide 4
Literature Survey 2 of 4
No | Author, Year | Problem | Method | Data / tests | Finding | Scope limit
6 | Yusubov & Bekirova 2023 | Variable PV output and demand | Power/SOC rules + load shedding | Standalone DC microgrid simulations | Coordinates loads within SOC bounds | No physical validation reported
7 | Basantes et al. 2023 | Dispatch cost and battery limits | Hierarchical control + predictive optimisation | Simulink + FICO Xpress scenarios | Reduces simulated operating cost | Battery degradation model deferred
8 | Sepehrzad et al. 2023 | Converter fluctuations and power sharing | Distributed MDMPC | Simulation, HIL and experiment | Reduces converter fluctuations | Complex converter control
9 | Khawaja et al. 2023 | PV / battery / diesel cost | Economic sizing + Q-learning | MATLAB with Amman profiles | Lowers cost and diesel use | Training and profile data required
10 | Singh & Maulik 2023 | Correlated load and supply | Probabilistic optimisation | Ten-bus DC network simulations | Reduces expected cost and losses | Grid-connected study
Notes: These studies motivate our design choices. Scope limits describe applicability to this project unless explicitly attributed to the authors. WattSense does not claim to outperform these methods.
[6] E. Yusubov and L. Bekirova, 'A standalone DC microgrid energy management strategy using the battery state of charge,' Informatyka, Automatyka, Pomiary w Gospodarce i Ochronie Środowiska, vol. 13, no. 3, pp. 75-78, 2023, doi: 10.35784/iapgos.5320.
https://ph.pollub.pl/index.php/iapgos/en/article/view/5320
Evidence: The publisher abstract explicitly combines available-source power, demand and SOC with load-shedding capability and evaluates an algorithm by simulation. Although authors claim battery-life benefits, the row deliberately uses SOC-limit coordination and does not present lifetime extension as measured cycling data.
[7] J. A. Basantes, D. E. Paredes, J. R. Llanos, D. E. Ortiz, and C. D. Burgos, 'Energy Management System (EMS) Based on Model Predictive Control (MPC) for an Isolated DC Microgrid,' Energies, vol. 16, no. 6, Art. 2912, 2023, doi: 10.3390/en16062912.
https://www.mdpi.com/1996-1073/16/6/2912
Evidence: Metadata/byline was confirmed from the primary published PDF hosted in a research repository. The study compares with/without EMS under radiation and demand disturbances. Its conclusions explicitly defer battery-degradation modeling and diesel-start constraints to future work. Real-time feedback here is within the simulated coupled control system; do not call it real hardware measurement.
[8] R. Sepehrzad, J. Ghafourian, A. Hedayatnia, A. Al-Durrad, and M. H. Khooban, 'Experimental and developed DC microgrid energy management integrated with battery energy storage based on multiple dynamic matrix model predictive control,' Journal of Energy Storage, vol. 74, Part A, Art. 109282, 2023, doi: 10.1016/j.est.2023.109282.
https://www.sciencedirect.com/science/article/pii/S2352152X23026804
Evidence: Both institutional and publisher abstracts describe an HIL environment plus a Micro Lab Box/dSPACE DS1202 experimental setup. The row does not invent sample sizes or transfer their transient results to WattSense. WattSense is a supervisory fan switch; it does not implement converter-level distributed predictive control.
[9] Y. Khawaja, I. Qiqieh, J. Alzubi, O. Alzubi, A. Allahham, and D. Giaouris, 'Design of cost-based sizing and energy management framework for standalone microgrid using reinforcement learning,' Solar Energy, vol. 251, pp. 249-260, 2023, doi: 10.1016/j.solener.2023.01.027.
https://www.sciencedirect.com/science/article/pii/S0038092X23000336
Evidence: Publisher methods text explicitly says MATLAB R2021a simulations, hourly PV profiles for Amman based on NREL and forecast-based rural load profiles. Therefore the row does not call these measured hardware results. The limitation is applicability: this optimisation workflow requires input profiles/training beyond WattSense's deterministic two-load policy.
[10] A. Singh and A. Maulik, 'DC Microgrid energy management with correlated uncertainties,' Sustainable Energy, Grids and Networks, vol. 35, Art. 101137, 2023, doi: 10.1016/j.segan.2023.101137.
https://www.sciencedirect.com/science/article/pii/S2352467723001455
Evidence: The primary page explicitly states a ten-bus simulated test network, probabilistic point estimates with correlation handling, and sufficient historical input data assumed. Its conclusion says grid-connected. This is contextual prior art for uncertainty handling, not a direct small standalone prototype baseline. Do not claim WattSense implements its optimisation or uncertainty model.
Sources

## Slide 5
Literature Survey 3 of 4
No | Author, Year | Problem | Method | Data / tests | Finding | Scope limit
11 | Movassagh et al. 2021 | Accumulated SOC error | Analytical error decomposition | Error models and simulations | Four error sources quantified | Current and initial-SOC errors
12 | Zhang et al. 2018 | Changing battery model parameters | Decoupled weighted RLS | Lithium-ion cell measurements | Separates fast / slow dynamics | Characterize our actual pack first
13 | Gismero et al. 2020 | Charge drift and capacity aging | Coulomb counting, OCV reset, RLS | Aged NMC cells; dynamic loads | OCV resets limit accumulated drift | Rest time and chemistry matter
14 | Yang et al. 2021 | SOC and parameter coupling | Separated RLS + EKF | 18650 data at varied temperature | Lower error than conventional RLS | Needs characterized model and data
15 | Rzepka et al. 2021 | Empirical tuning and sensor noise | ECM + hysteresis + EKF tuning | Cell estimator experiment | Tuning improves estimator stability | Needs noise estimates
Notes: These studies motivate our design choices. Scope limits describe applicability to this project unless explicitly attributed to the authors. WattSense does not claim to outperform these methods.
[11] K. Movassagh, A. Raihan, B. Balasingam, and K. Pattipati, "A Critical Look at Coulomb Counting Approach for State of Charge Estimation in Batteries," Energies, vol. 14, no. 14, Art. 4074, 2021, doi: 10.3390/en14144074.
https://doi.org/10.3390/en14144074
Evidence: Separates current-measurement, integration, capacity and timing errors. Its results do not establish a WattSense SOC accuracy figure. Calibration/initialization is our design implication.
[12] C. Zhang, W. Allafi, Q. Dinh, P. Ascencio, and J. Marco, "Online estimation of battery equivalent circuit model parameters and state of charge using decoupled least squares technique," Energy, vol. 142, pp. 678–688, 2018, doi: 10.1016/j.energy.2017.10.043.
https://doi.org/10.1016/j.energy.2017.10.043
Evidence: Published in 2018 despite 2017 in DOI. Supports caution about fixed assumed plant parameters. WattSense has not implemented this estimator or measured its pack parameters.
[13] A. Gismero, E. Schaltz, and D.-I. Stroe, "Recursive State of Charge and State of Health Estimation Method for Lithium-Ion Batteries Based on Coulomb Counting and Open Circuit Voltage," Energies, vol. 13, no. 7, Art. 1811, 2020, doi: 10.3390/en13071811.
https://doi.org/10.3390/en13071811
Evidence: Tested aged cells with changing current/temperature. The paper explicitly identifies insufficient relaxation as a capacity-estimation issue. Our LFP pack cannot inherit its NMC OCV map or accuracy.
[14] K. Yang, Y. Tang, and Z. Zhang, "Parameter Identification and State-of-Charge Estimation for Lithium-Ion Batteries Using Separated Time Scales and Extended Kalman Filter," Energies, vol. 14, no. 4, Art. 1054, 2021, doi: 10.3390/en14041054.
https://doi.org/10.3390/en14041054
Evidence: The result is specific to its datasets and estimator. It informs future characterization; WattSense currently uses a simpler current-integration policy, not the published RLS/EKF method.
[15] B. Rzepka, S. Bischof, and T. Blank, "Implementing an Extended Kalman Filter for SoC Estimation of a Li-Ion Battery with Hysteresis: A Step-by-Step Guide," Energies, vol. 14, no. 13, Art. 3733, 2021, doi: 10.3390/en14133733.
https://doi.org/10.3390/en14133733
Evidence: Conclusions compare systematic and rough filter tuning. This is a future-estimator reference, not evidence that WattSense's INA219/current integration achieves the paper's accuracy.
Sources

## Slide 6
Literature Survey 4 of 4
No | Author, Year | Problem | Method | Data / tests | Finding | Scope limit
16 | Zine et al. 2022 | Simple real-time SOC estimation | Current integration | Lead-acid bench tests | Bench SOC workflow | LFP tests still needed
17 | Fahmy et al. 2023 | SOC under changing battery conditions | Coulomb counting plus adaptive UKF | 2.6 Ah Panasonic simulations | Lower simulated error in comparisons | Numerical results only
18 | Wang et al. 2023 | Voltage plateau and temperature variation | Temperature ECM; improved EKF | LFP chamber / load tests | Temperature-aware estimate | Needs pack-specific data
19 | Turkmanović et al. 2024 | Estimator energy versus accuracy | Two EKFs at varied rates | PC accuracy + STM32H7 timing | Sample-rate trade-off | ESP32 timing unknown
20 | Bampi et al. 2025 | Battery parameter testing | Electronic load + ECM / EKF | LTO cell + ESP32 rig | Parameter and SOC estimates | Different test rig
Notes: These studies motivate our design choices. Scope limits describe applicability to this project unless explicitly attributed to the authors. WattSense does not claim to outperform these methods.
[16] B. Zine, H. Bia, A. Benmouna, M. Becherif, and M. Iqbal, "Experimentally Validated Coulomb Counting Method for Battery State-of-Charge Estimation under Variable Current Profiles," Energies, vol. 15, no. 21, Art. 8172, 2022, doi: 10.3390/en15218172.
https://doi.org/10.3390/en15218172
Evidence: The broad Li-ion discussion in the abstract must not be mistaken for our 4S LFP validation. Initial SOC and suitable measurements are needed; this study is a practical procedure reference.
[17] H. M. Fahmy et al., "Hybrid State of Charge Estimation of Lithium-Ion Battery Using the Coulomb Counting Method and an Adaptive Unscented Kalman Filter," Energies, vol. 16, no. 14, Art. 5558, 2023, doi: 10.3390/en16145558.
https://doi.org/10.3390/en16145558
Evidence: The abstract explicitly labels numerical simulations and describes parameter fitting with African Vultures Optimization. The table includes only the estimator core. Do not present this as a physical WattSense comparison.
[18] M. Wang, G. Wang, Z. Xiao, Y. Sun, and Y. Zheng, "State of Charge Estimation of LiFePO4 in Various Temperature Scenarios," Batteries, vol. 9, no. 1, Art. 43, 2023, doi: 10.3390/batteries9010043.
https://doi.org/10.3390/batteries9010043
Evidence: Direct chemistry relevance. Temperature-dependent capacity and the flat OCV region motivate measuring the actual pack instead of relying on the assumed teaching curve. WattSense's fixed-temperature simulation does not reproduce these tests.
[19] H. Turkmanović, I. Popović, and V. Rajović, "Toward Energy Efficient Battery State of Charge Estimation on Embedded Platforms," Electronics, vol. 13, no. 21, Art. 4256, 2024, doi: 10.3390/electronics13214256.
https://doi.org/10.3390/electronics13214256
Evidence: Contrasts Rint and second-order RC EKFs and connects estimator rate to energy cost. Its reported savings cannot be copied to the ESP32; our 0.8 W controller load remains an assumption awaiting measurement.
[20] S. Bampi, G. Waltrich, and A. Vaccari, "Electronic Load for Parameter Characterization in Equivalent Circuit Models of Lithium-Ion Batteries," Eletrônica de Potência, vol. 30, Art. e202521, 2025, doi: 10.18618/REP.e202521.
https://doi.org/10.18618/REP.e202521
Evidence: An electronic-load instrument characterized a lithium-titanate cell and supplied data to EKF SOC estimation. WattSense uses a protected LFP pack with a switched fan, not this high-current characterization load.
Sources

## Slide 7
Research Gap and Project Focus
Published priority control and SOC methods already exist.
Many studies target larger microgrids or need battery characterisation and training data.
Our project needs a small, inspectable implementation with a clear load-service tradeoff.
Voltage drop, fan startup and sensor errors can limit an otherwise valid control rule.
We combine a local controller, a routed interface PCB and reproducible tests, then validate them on hardware.
Notes: This is an implementation gap for our project constraints, not a claim that the research community lacks priority shedding. The planned prototype can test real calibration, startup and runtime limits that current simulations cannot establish.
Sources
paper/src/manuscript.json, C003–C006
Literature survey references [1]–[20]

## Slide 8
Problem Statement
Objectives
Design and evaluate a low-cost battery monitor that preserves essential lamp service by disconnecting an optional fan when the estimated backup becomes limited.
Measure signed battery current, load power and surface temperature.
Estimate charge and remaining runtime from a valid reference.
Implement fan shedding, explicit restore and fault handling.
Compare lamp and fan service, then calibrate and test the assembled system.
Notes: The spending plan targets less than ₹10,000, but delivered quotations have not yet established affordability. Runtime is a heuristic, not a guaranteed minimum. Cell-level protection remains with the purchased BMS.
Sources
WATTSENSE_PROJECT_BLUEPRINT.md
docs/TEST_PLAN.md

## Slide 9
Methodology and System Architecture
Protected pack
Purchased BMS
Interface PCB
Current sensors
External buck
5 V output
Essential lamp
Unswitched
Optional fan
Q1 return switch
ESP32
SOC and control
Local dashboard
USB and CSV
DS18B20 temperature input
Rev B: four layers
100 × 90 mm
Not fabricated
Integrate current to estimate SOC and usable runtime.
Fan OFF after 3 s below 3 h.
Restore: requested, prospective ≥3.25 h, operating limits valid.
Notes: The custom board measures signed battery current (U1), load input (U2) and optional charging current (U3). The purchased protected 4S LiFePO4 pack and matched charger supply cell protection and charging. U3 readout and solar are disabled initially. Essential lamp is unswitched, so reserve tests require supervised external stopping. Solid arrows denote power and dashed arrows denote data/control. Shared return, fuses and charger routing are omitted from this conceptual diagram. DS18B20 supplies surface temperature. SOC begins unknown and needs a verified full-charge reference. A sample gap >2 s or invalid sample turns the optional output off and invalidates charge tracking. Restore requires explicit request, prospective runtime at least3.25 h and all operating gates. Intended ceilings:2 A battery,1.5 A total5 V, measured starter branches≤0.6 A each. Configured CAD checks pass; six generic connector footprint-filter warnings appear with all ignored categories enabled. Actual assigned footprints, nets, pitch and drills were independently checked. The board is not fabricated.
Sources
hardware/REFERENCE_WIRING.md
firmware/include/controller.h
firmware/include/config.h
docs/evidence/recheck-2026-09-30/hardware/FINDINGS.md

## Slide 10
Data Collection and Validation
Available evidence | Next physical measurement
Synthetic battery and policy CSV traces | Independent meter and sensor log
18 deterministic scenario pairs | Measured capacity and converter efficiency
Six behavioral SPICE startup cases | 5 V, fan and 3.3 V scope traces
45 Python tests, 67 C++ assertions | Calibration and repeated runtime trials
Both firmware builds pass. 12,000 host policy steps agree.
3 of 6 startup cases fail the provisional 4.75 V rail screen.
No physical measurements yet.
Next: assemble, calibrate, test startup, temperature and runtime.
Notes: Current data are synthetic model traces, not physical observations. The18 pairs vary assumed capacity, efficiency and battery resistance; they are deterministic scenarios, not confidence intervals. The12,000 comparisons use host-compiled C++ versus Python, not ESP32 execution. Both production and bring-up targets build; production arming remains disabled. The reduced startup simulations give common-rail/fan minima: S1 4.824746/4.677085 V, S2 4.756409/4.473916 V, S3 2.994660/2.735565 V, S4 identical minima with2200 µF, S5 4.693761/4.287662 V, S6 4.790716/4.551236 V. Fan-start/source-limit currents: S1 .6/2 A, S2 1.2/2 A, S3–S4 1.8/1.5 A, S5 1.8/3 A, S6 1/2 A. Other cases use470 µF. S3,S4,S5 fail the provisional4.75 V rail screen. This screen is neither an actual selected-fan specification nor an ESP32 reset threshold. More capacitance cannot fix sustained source shortage. Models do not establish converter/BLDC/thermal performance. Hardware logs must include timestamps, independent readings, load state and temperature.
Sources
docs/RECHECK_2026-09-30.md
simulations/results/hardware-summary.json
docs/TEST_PLAN.md

## Slide 11
Expected Outcomes and Evaluation
Chart: Simulated service (h)
| Lamp service | Fan service
Both loads retained | 5.4764 | 5.4764
Priority control | 7.8836 | 2.4936
Lamp +43.96%
Fan −54.47%
Service tradeoff
Calibration targets
Voltage: ±1%
Current: ±(3% of reference
+ 10 mA)
Measurement pending
Model: 6 Ah, 68% to 20% SOC, 90% efficiency, zero charging.
Loads: 2.5 W lamp + 2.5 W fan + 0.8 W controller.
Final outcome: assembled prototype with calibrated logs,
repeatable load control and measured service comparisons.
Notes: The chart reports a Python reference controller coupled to a nonideal battery/load model. Baseline lamp/fan service is5.476388889 h. Priority lamp service is7.883611111 h and fan service2.493611111 h. Lamp+43.956378% accompanies fan−54.466142%; this reallocates service and does not add battery capacity or show an equal-service efficiency gain. Values in the editable chart workbook are rounded to six decimals; raw values remain in hardware-summary.json. Runtime depends on assumed capacity, OCV, resistance, efficiency and known current. Hardware has not established these runtimes. Calibration target is±1% voltage and±(3% of independent reference current +10 mA). Verify these targets with held-out readings and instrument uncertainty. Also test3 s low-runtime trigger, invalid-reading OFF, explicit restore, startup rails, temperature and repeated matched baseline/priority discharge. Use supervised external stopping because the lamp is unswitched.
Sources
simulations/results/hardware-summary.json
simulations/hardware-assumptions.json
docs/TEST_PLAN.md

## Slide 12
Project Timeline
Stage | Work and expected evidence
By 3 Oct 2026 | Review 3: design, software demo and simulations
October 2026 | Confirm parts and quotes, then assemble on bench supply
Nov–Dec 2026 | Calibration, fan startup and loaded thermal tests
Next semester | Repeated baseline/priority trials and enclosure
Final submission | Working prototype, measured results and final report
Notes: Review3 is3 October2026 as supplied. The final project submission is next semester. The listed months are planning stages, not confirmed deliveries. Initial allocation₹9,700 includes a₹700 contingency, no funded re-spin and no solar purchase. Scope is one custom interface board and a purchased protected BMS pack.
Sources
User review date,1 October2026
docs/NEXT_STEPS.md
hardware/BUYING_PLAN_PUNE.md

## Slide 13
References
[1] Marahatta et al., 2021
10.1016/j.egyr.2020.11.030
[2] Rajbhandari et al., 2024
10.1049/stg2.12151
[3] Bai et al., 2020
10.3390/app10072544
[4] Lv et al., 2021
10.3390/electronics10070834
[5] Guo & Kors, 2021
10.3390/electronics10131562
[6] Yusubov & Bekirova, 2023
10.35784/iapgos.5320
[7] Basantes et al., 2023
10.3390/en16062912
[8] Sepehrzad et al., 2023
10.1016/j.est.2023.109282
[9] Khawaja et al., 2023
10.1016/j.solener.2023.01.027
[10] Singh & Maulik, 2023
10.1016/j.segan.2023.101137
[11] Movassagh et al., 2021
10.3390/en14144074
[12] Zhang et al., 2018
10.1016/j.energy.2017.10.043
[13] Gismero et al., 2020
10.3390/en13071811
[14] Yang et al., 2021
10.3390/en14041054
[15] Rzepka et al., 2021
10.3390/en14133733
[16] Zine et al., 2022
10.3390/en15218172
[17] Fahmy et al., 2023
10.3390/en16145558
[18] Wang et al., 2023
10.3390/batteries9010043
[19] Turkmanović et al., 2024
10.3390/electronics13214256
[20] Bampi et al., 2025
10.18618/REP.e202521
Notes: [1] A. Marahatta, Y. Rajbhandari, A. Shrestha, A. Singh, A. Gachhadar, and A. Thapa, 'Priority-based low voltage DC microgrid system for rural electrification,' Energy Reports, vol. 7, pp. 43-51, 2021, doi: 10.1016/j.egyr.2020.11.030.
https://www.sciencedirect.com/science/article/pii/S2352484720314554
Evidence: Publisher abstract, retrieved 2026-10-01; existing paper/evidence/literature-review.json, source marahatta2021 (2026-09-30). Earlier author-uploaded paper section 2.2.2 and Table 3 were checked in that record.
[2] Y. Rajbhandari, A. Marahatta, A. Shrestha, A. Gachhadar, A. Thapa, F. Gonzalez-Longatt, and P. Korba, 'Enhanced demand side management for solar-based isolated microgrid system: Load prioritisation and energy optimisation,' IET Smart Grid, vol. 7, no. 3, pp. 294-313, 2024, doi: 10.1049/stg2.12151.
https://ietresearch.onlinelibrary.wiley.com/doi/10.1049/stg2.12151
Evidence: Publisher abstract; section 4 Discussion and Conclusions; issue citation. Publisher content retrieved through indexed primary page 2026-10-01. Saved literature-review.json also checked.
[3] W. Bai, M. Sechilariu, and F. Locment, 'DC Microgrid System Modeling and Simulation Based on a Specific Algorithm for Grid-Connected and Islanded Modes with Real-Time Demand-Side Management Optimization,' Applied Sciences, vol. 10, no. 7, Art. 2544, 2020, doi: 10.3390/app10072544.
https://www.mdpi.com/2076-3417/10/7/2544
Evidence: Publisher PDF pp. 1-3 abstract/contributions; section 2 introduction (p. 3), section 2.6 DC Load (p. 6); doi and byline on p. 1.
[4] J. Lv, X. Wang, G. Wang, and Y. Song, 'Research on Control Strategy of Isolated DC Microgrid Based on SOC of Energy Storage System,' Electronics, vol. 10, no. 7, Art. 834, 2021, doi: 10.3390/electronics10070834.
https://www.mdpi.com/2079-9292/10/7/834
Evidence: Publisher indexed full text: byline/abstract, section 4 Simulation and Discussion, section 4.2, Table 2, section 5 Conclusions.
[5] L. Guo and J. Kors, Jr., 'Design of a Laboratory Scale Solar Microgrid Cyber-Physical System for Education,' Electronics, vol. 10, no. 13, Art. 1562, 2021, doi: 10.3390/electronics10131562.
https://www.mdpi.com/2079-9292/10/13/1562
Evidence: Publisher indexed full text: title/byline, section 2 system design, section 4 GUI, section 6 Experimental Results, section 7 Educational Assessment and section 8 conclusions.
[6] E. Yusubov and L. Bekirova, 'A standalone DC microgrid energy management strategy using the battery state of charge,' Informatyka, Automatyka, Pomiary w Gospodarce i Ochronie Środowiska, vol. 13, no. 3, pp. 75-78, 2023, doi: 10.35784/iapgos.5320.
https://ph.pollub.pl/index.php/iapgos/en/article/view/5320
Evidence: Publisher landing page abstract and citation, published 30 September 2023; publisher four-page PDF opened for primary source confirmation.
[7] J. A. Basantes, D. E. Paredes, J. R. Llanos, D. E. Ortiz, and C. D. Burgos, 'Energy Management System (EMS) Based on Model Predictive Control (MPC) for an Isolated DC Microgrid,' Energies, vol. 16, no. 6, Art. 2912, 2023, doi: 10.3390/en16062912.
https://www.mdpi.com/1996-1073/16/6/2912
Evidence: Publisher indexed sections 4 Results and 5 Conclusions; published PDF at LAPSE repository pp. 1 (metadata), 12-18 (results and conclusions).
[8] R. Sepehrzad, J. Ghafourian, A. Hedayatnia, A. Al-Durrad, and M. H. Khooban, 'Experimental and developed DC microgrid energy management integrated with battery energy storage based on multiple dynamic matrix model predictive control,' Journal of Energy Storage, vol. 74, Part A, Art. 109282, 2023, doi: 10.1016/j.est.2023.109282.
https://www.sciencedirect.com/science/article/pii/S2352152X23026804
Evidence: Aarhus University institutional record: authors, peer-review flag, abstract paragraphs 1-4, citation and DOI. Publisher abstract was independently retrieved.
[9] Y. Khawaja, I. Qiqieh, J. Alzubi, O. Alzubi, A. Allahham, and D. Giaouris, 'Design of cost-based sizing and energy management framework for standalone microgrid using reinforcement learning,' Solar Energy, vol. 251, pp. 249-260, 2023, doi: 10.1016/j.solener.2023.01.027.
https://www.sciencedirect.com/science/article/pii/S0038092X23000336
Evidence: Publisher title/byline/abstract and Experimental results section; 15-page author manuscript opened from Newcastle staff repository, title page and abstract.
[10] A. Singh and A. Maulik, 'DC Microgrid energy management with correlated uncertainties,' Sustainable Energy, Grids and Networks, vol. 35, Art. 101137, 2023, doi: 10.1016/j.segan.2023.101137.
https://www.sciencedirect.com/science/article/pii/S2352467723001455
Evidence: Publisher indexed article title/byline/abstract; System modelling assumptions; Test system; Conclusions.
[11] K. Movassagh, A. Raihan, B. Balasingam, and K. Pattipati, "A Critical Look at Coulomb Counting Approach for State of Charge Estimation in Batteries," Energies, vol. 14, no. 14, Art. 4074, 2021, doi: 10.3390/en14144074.
https://doi.org/10.3390/en14144074
Evidence: Existing primary-source record paper/evidence/literature-review.json, id movassagh2021; NASA-hosted manuscript abstract and error-analysis sections.
[12] C. Zhang, W. Allafi, Q. Dinh, P. Ascencio, and J. Marco, "Online estimation of battery equivalent circuit model parameters and state of charge using decoupled least squares technique," Energy, vol. 142, pp. 678–688, 2018, doi: 10.1016/j.energy.2017.10.043.
https://doi.org/10.1016/j.energy.2017.10.043
Evidence: Existing primary-source record paper/evidence/literature-review.json, id zhang2018; abstract, experimental section 4.1 and discussion 6.1.
[13] A. Gismero, E. Schaltz, and D.-I. Stroe, "Recursive State of Charge and State of Health Estimation Method for Lithium-Ion Batteries Based on Coulomb Counting and Open Circuit Voltage," Energies, vol. 13, no. 7, Art. 1811, 2020, doi: 10.3390/en13071811.
https://doi.org/10.3390/en13071811
Evidence: Aalborg-hosted version of record: section 2 identifies 3.4 Ah NMC cells; sections 3–5 describe efficiency compensation, OCV reset and RLS; section 6 discusses relaxation-time dependence.
[14] K. Yang, Y. Tang, and Z. Zhang, "Parameter Identification and State-of-Charge Estimation for Lithium-Ion Batteries Using Separated Time Scales and Extended Kalman Filter," Energies, vol. 14, no. 4, Art. 1054, 2021, doi: 10.3390/en14041054.
https://doi.org/10.3390/en14041054
Evidence: Published-paper PDF: section 3/Table 1 states University of Maryland 2 Ah LiNiMnCo/graphite data; OCV and DST tests at 0, 25 and 45 °C; section 3.2.2 and conclusion compare against RLS.
[15] B. Rzepka, S. Bischof, and T. Blank, "Implementing an Extended Kalman Filter for SoC Estimation of a Li-Ion Battery with Hysteresis: A Step-by-Step Guide," Energies, vol. 14, no. 13, Art. 3733, 2021, doi: 10.3390/en14133733.
https://doi.org/10.3390/en14133733
Evidence: Publisher retrieved sections 2, 3, 5, 6.1 and 7; KIT institutional bibliographic record. Section 6.1 describes a cell estimator operating within a 96-cell system using AURIX/LTC6811/fluxgate hardware.
[16] B. Zine, H. Bia, A. Benmouna, M. Becherif, and M. Iqbal, "Experimentally Validated Coulomb Counting Method for Battery State-of-Charge Estimation under Variable Current Profiles," Energies, vol. 15, no. 21, Art. 8172, 2022, doi: 10.3390/en15218172.
https://doi.org/10.3390/en15218172
Evidence: Publisher retrieved abstract, section 3 and concluding paragraphs. Conclusion explicitly describes experimental validation using a domestic lead-acid battery.
[17] H. M. Fahmy et al., "Hybrid State of Charge Estimation of Lithium-Ion Battery Using the Coulomb Counting Method and an Adaptive Unscented Kalman Filter," Energies, vol. 16, no. 14, Art. 5558, 2023, doi: 10.3390/en16145558.
https://doi.org/10.3390/en16145558
Evidence: Opened University of Jaén publication record: abstract, citation and author metadata; university-hosted paper title-page retrieval confirms article byline.
[18] M. Wang, G. Wang, Z. Xiao, Y. Sun, and Y. Zheng, "State of Charge Estimation of LiFePO4 in Various Temperature Scenarios," Batteries, vol. 9, no. 1, Art. 43, 2023, doi: 10.3390/batteries9010043.
https://doi.org/10.3390/batteries9010043
Evidence: Publisher retrieved abstract and sections 2 and 3.1–3.4: temperature-dependent ECM, PSO parameter fitting, improved EKF, Lishen LFP tests, HPPC and variable-temperature NEDC experiments.
[19] H. Turkmanović, I. Popović, and V. Rajović, "Toward Energy Efficient Battery State of Charge Estimation on Embedded Platforms," Electronics, vol. 13, no. 21, Art. 4256, 2024, doi: 10.3390/electronics13214256.
https://doi.org/10.3390/electronics13214256
Evidence: Publisher retrieved abstract, introduction, sections 3 and 7; implementation description identifies STM32H747XIH6 on STM32H7-DISCO. Accuracy and run-cycle duration are evaluated separately.
[20] S. Bampi, G. Waltrich, and A. Vaccari, "Electronic Load for Parameter Characterization in Equivalent Circuit Models of Lithium-Ion Batteries," Eletrônica de Potência, vol. 30, Art. e202521, 2025, doi: 10.18618/REP.e202521.
https://doi.org/10.18618/REP.e202521
Evidence: Opened SciELO publisher PDF: page 1 abstract, section II ECM, section IV-A ESP32 prototype, sections V–VI load and cell-parameterization results.
Sources

## Slide 14: Thank You Questions and Discussion
Notes: Expected questions: Why use a purchased BMS? It supplies cell protection while our board monitors energy and controls a fan. What is demonstrated now? Software, CAD and simulation. What comes next? Parts selection, assembly, calibration and physical validation.
Sources