## Slide 1
KJEI’s, Trinity Academy of Engineering
Department of Electronics and
Telecommunication Engineering
Academic Year 2026–27 Semester I
Project Review 3
1
    Name of Students
    Dhanesh Chaudhari (4114)
    Yash Ahire (4101)
    Mrudula Pagar (4212)
    Ujjwal Kshirsagar (4154)
Date: 3 October 2026
WattSense
Battery Energy and Runtime Estimation
with Load Signature Guidance
Under the guidance of
Mahesh Sapte
Group 7
Notes: WattSense is a battery-mounted, battery-powered monitoring and advisory device. It estimates charge, usable energy and backup time, then uses selected load signatures and user priorities to recommend which optional load to turn off. Solar charging or a compatible AC-to-DC battery charger can charge the battery. The battery supplies DC loads through appropriate converters and AC loads through an inverter. Group 7: Dhanesh Chaudhari 4114, Yash Ahire 4101, Mrudula Pagar 4212, Ujjwal Kshirsagar 4154. Guide: Mahesh Sapte. Review 3: 3 October 2026. Current evidence remains DC firmware, local dashboard, simulations and unbuilt Rev B CAD. The combined physical device, AC integration and trained signatures are pending.
Sources
sih 2026 shubham.pptx
User clarification, 3 October 2026

## Slide 2
2
Introduction and Topic Overview
WattSense mounts near the battery and runs from a regulated battery supply.
Review 3: DC firmware, dashboard and PCB design prepared.
Next stage: integrated sensing, learned profiles and guidance validation.
Estimate battery charge, usable energy and remaining backup time.
Support solar charging or a compatible AC-to-DC battery charger.
Support DC loads through converters and AC loads through an inverter.
Use load signatures and priorities to suggest what to turn off.
Notes: The original SIH idea centres on a battery-system monitor, not a standalone mains appliance meter. WattSense is housed near the battery and powered from the monitored protected DC bus through a qualified regulator. It measures whole-battery signed current, voltage and temperature. Its power draw is included in total battery demand. Support AC and DC loads through external suitably rated conversion hardware. Solar panels need a compatible solar charge controller; mains needs a chemistry-compatible isolated AC-to-DC battery charger. Select one approved charging path initially. The monitoring device does not replace the battery BMS, charger or inverter. Recommendations are advisory: the user turns off a selected optional load. A custom BMS and automatic mains switching are not required.
Sources
sih 2026 shubham.pptx
hardware/REFERENCE_WIRING.md
hardware/PCB_REQUIREMENTS.md

## Slide 3
3
Literature Survey 1 of 4
No | Research Paper / Author / Year | Problem | Method | Data / tests | Finding | Scope limit
1 | A Scalable Real-Time Non-Intrusive Load Monitoring System for the Estimation of Household Appliance Power Consumption Athanasiadis et al., 2021 | Load energy estimation | Events + CNN + power estimate | Reported experimental evaluation | Real-time consumption estimates | Transient data needed
2 | Explainability-Informed Feature Selection and Performance Prediction for Nonintrusive Load Monitoring Mollel et al., 2023 | Unclear load classification | Decision trees + explanations | REFIT to UK-DALE transfer tests | Feature selection improves classification | Cross-house transfer needs testing
3 | Machine Learning Models for Non-Intrusive Load Monitoring: A Systematic Review and Meta-Analysis Jaime et al., 2026 | Variable evaluation methods | PRISMA + meta-analysis | 30 studies; 2017-2024 publications | Performance varies across study settings | Heterogeneous study methods
4 | Non-Intrusive Load Monitoring: A Systematic Review of Methods, Scenario-Specific Challenges, and Pathways to Practical Deployment Xiang et al., 2026 | Practical deployment barriers | Event/state methods; scenario review | Review of published NILM studies | Maps deployment needs and trade-offs | Unknown loads and transfer limits
5 | A Non-Intrusive Load Identification Method Based on the Fusion of Steady-State Features and Lightweight Network Li et al., 2026 | Similar load signatures | AC V-I + dual-branch network | PLAID AC appliance recordings | Feature fusion aids classification | Requires AC waveforms
Notes: These papers inform the proposed project. Findings belong to the cited authors and are not WattSense results. Scope limits describe applicability to the proposed AC signature and DC battery subsystems.
Li et al. use captured AC voltage-current trajectories. A low-rate RMS/real-power meter alone does not provide those waveforms; the planned first classifier uses slow power features appropriate to the selected meter.
[1] Christos Athanasiadis, Dimitrios Doukas, Theofilos Papadopoulos, Antonios Chrysopoulos, "A Scalable Real-Time Non-Intrusive Load Monitoring System for the Estimation of Household Appliance Power Consumption", Energies, vol. 14, no. 3, Art. 767, 2021, doi: 10.3390/en14030767.
https://www.mdpi.com/1996-1073/14/3/767
Evidence: Primary publisher abstract states three blocks: event detection, CNN classifier and power estimator using active-power turn-on transients. It reports computational/memory efficiency qualitatively. Cached full-page excerpt ends within the introduction, so dataset names, exact sampling rates and numerical performance are not asserted. The limitation cell is an applicability inference: this method needs suitable transient measurements and an already trained target-appliance classifier. It does not validate WattSense, universal detection or zero-configuration deployment.
[2] Rachel Stephen Mollel, Lina Stankovic, Vladimir Stankovic, "Explainability-Informed Feature Selection and Performance Prediction for Nonintrusive Load Monitoring", Sensors, vol. 23, no. 10, Art. 4845, 2023, doi: 10.3390/s23104845.
https://www.mdpi.com/1424-8220/23/10/4845
Evidence: Publisher abstract describes interpretable decision-tree classification, local/global feature importance, REFIT training and unseen same-house/UK-DALE-house evaluation. It reports class-specific improvements, but the displayed row deliberately transfers no percentage to WattSense. Cross-house transfer testing is a design implication drawn from the study setting; the current DC INA219 system cannot inherit its household-data performance.
[3] Herman Cristiano Jaime, Adler Diniz de Souza, Raphael Carlos Santos Machado, Otávio de Souza Martins Gomes, "Machine Learning Models for Non-Intrusive Load Monitoring: A Systematic Review and Meta-Analysis", Inventions, vol. 11, no. 2, Art. 29, 2026, doi: 10.3390/inventions11020029.
https://www.mdpi.com/2411-5134/11/2/29
Evidence: This is a systematic review and meta-analysis, not a new hardware trial. The publisher abstract states 30 eligible studies, random-effects pooling of F1 scores and substantial heterogeneity. Hybrid models had high pooled scores with limited study support; traditional models had broader validation. No pooled score is used as a WattSense result. Issue citation year is 2026; covered primary-study period is 2017-2024.
[4] Haotian Xiang, Wenjing Su, Yi Zong, "Non-Intrusive Load Monitoring: A Systematic Review of Methods, Scenario-Specific Challenges, and Pathways to Practical Deployment", Energies, vol. 19, no. 8, Art. 1883, 2026, doi: 10.3390/en19081883.
https://www.mdpi.com/1996-1073/19/8/1883
Evidence: This is a systematic review/framework, not new hardware validation. Its abstract explicitly identifies real-time/accuracy trade-offs, privacy, unknown loads, behaviour modelling, data quality, transferability, integration and cost. The row is a qualitative synthesis and does not assert a dataset, new classifier or measured accuracy for this review. Relevant to scoping a small known-load prototype with an unknown/ambiguous output.
[5] Yiran Li, Yan Li, Peng Han, "A Non-Intrusive Load Identification Method Based on the Fusion of Steady-State Features and Lightweight Network", Energies, vol. 19, no. 13, Art. 3131, 2026, doi: 10.3390/en19133131.
https://www.mdpi.com/1996-1073/19/13/3131
Evidence: Publisher abstract describes V-I trajectory images plus active/reactive power, trajectory area and slope, fused with a lightweight dual-branch network. Evaluation uses PLAID. The original abstract reports 95.35% recognition accuracy and 0.17M parameters, but these external results are not displayed or attributed to WattSense. This is an AC waveform-based method: the current INA219 DC voltage/current telemetry does not provide synchronised AC V-I trajectories, reactive power or waveform images. The limitation is an explicit sensor/method applicability comparison, not a defect demonstrated by the paper.
Sources
Current project context: a battery-mounted and battery-powered monitor/adviser. AC appliance signatures support battery demand and runtime guidance. Battery and microgrid papers support sensing, charge estimation and integration. Their results are external evidence, not WattSense measurements.

## Slide 4
4
Literature Survey 2 of 4
No | Research Paper / Author / Year | Problem | Method | Data / tests | Finding | Scope limit
6 | A Critical Look at Coulomb Counting Approach for State of Charge Estimation in Batteries Movassagh et al., 2021 | SOC error build-up | Analytical error decomposition | Error models and simulations | Quantifies four SOC error sources | Current and initial-SOC errors
7 | Online estimation of battery equivalent circuit model parameters and state of charge using decoupled least squares technique Zhang et al., 2018 | Changing battery model parameters | Decoupled weighted RLS | Lithium-ion cell measurements | Separates fast / slow dynamics | Actual pack data needed
8 | Recursive State of Charge and State of Health Estimation Method for Lithium-Ion Batteries Based on Coulomb Counting and Open Circuit Voltage Gismero et al., 2020 | Charge drift and capacity aging | Coulomb counting, OCV reset, RLS | Aged NMC cells; dynamic loads | OCV resets limit accumulated drift | Rest time and chemistry matter
9 | Parameter Identification and State-of-Charge Estimation for Lithium-Ion Batteries Using Separated Time Scales and Extended Kalman Filter Yang et al., 2021 | SOC and parameter coupling | Separated RLS + EKF | 18650 data at varied temperature | Lower error than conventional RLS | Needs characterized model and data
10 | Implementing an Extended Kalman Filter for SoC Estimation of a Li-Ion Battery with Hysteresis: A Step-by-Step Guide Rzepka et al., 2021 | Empirical tuning and sensor noise | Circuit + hysteresis + EKF tuning | Cell estimator experiment | Tuning improves estimator stability | Needs noise estimates
Notes: These papers inform the proposed project. Findings belong to the cited authors and are not WattSense results. Scope limits describe applicability to the proposed AC signature and DC battery subsystems.
Battery and microgrid studies provide subsystem context. Their particular chemistry, hardware, results and sampling cannot be transferred directly to the proposed household system.
[6] K. Movassagh, A. Raihan, B. Balasingam, and K. Pattipati, "A Critical Look at Coulomb Counting Approach for State of Charge Estimation in Batteries," Energies, vol. 14, no. 14, Art. 4074, 2021, doi: 10.3390/en14144074.
https://doi.org/10.3390/en14144074
Evidence: Separates current-measurement, integration, capacity and timing errors. Its results do not establish a WattSense SOC accuracy figure. Calibration/initialization is our design implication.
[7] C. Zhang, W. Allafi, Q. Dinh, P. Ascencio, and J. Marco, "Online estimation of battery equivalent circuit model parameters and state of charge using decoupled least squares technique," Energy, vol. 142, pp. 678–688, 2018, doi: 10.1016/j.energy.2017.10.043.
https://doi.org/10.1016/j.energy.2017.10.043
Evidence: Published in 2018 despite 2017 in DOI. Supports caution about fixed assumed plant parameters. WattSense has not implemented this estimator or measured its pack parameters.
[8] A. Gismero, E. Schaltz, and D.-I. Stroe, "Recursive State of Charge and State of Health Estimation Method for Lithium-Ion Batteries Based on Coulomb Counting and Open Circuit Voltage," Energies, vol. 13, no. 7, Art. 1811, 2020, doi: 10.3390/en13071811.
https://doi.org/10.3390/en13071811
Evidence: Tested aged cells with changing current/temperature. The paper explicitly identifies insufficient relaxation as a capacity-estimation issue. Our LFP pack cannot inherit its NMC OCV map or accuracy.
[9] K. Yang, Y. Tang, and Z. Zhang, "Parameter Identification and State-of-Charge Estimation for Lithium-Ion Batteries Using Separated Time Scales and Extended Kalman Filter," Energies, vol. 14, no. 4, Art. 1054, 2021, doi: 10.3390/en14041054.
https://doi.org/10.3390/en14041054
Evidence: The result is specific to its datasets and estimator. It informs future characterization; WattSense currently uses a simpler current-integration policy, not the published RLS/EKF method.
[10] B. Rzepka, S. Bischof, and T. Blank, "Implementing an Extended Kalman Filter for SoC Estimation of a Li-Ion Battery with Hysteresis: A Step-by-Step Guide," Energies, vol. 14, no. 13, Art. 3733, 2021, doi: 10.3390/en14133733.
https://doi.org/10.3390/en14133733
Evidence: Conclusions compare systematic and rough filter tuning. This is a future-estimator reference, not evidence that WattSense's INA219/current integration achieves the paper's accuracy.
Sources
Current project context: a battery-mounted and battery-powered monitor/adviser. AC appliance signatures support battery demand and runtime guidance. Battery and microgrid papers support sensing, charge estimation and integration. Their results are external evidence, not WattSense measurements.

## Slide 5
5
Literature Survey 3 of 4
No | Research Paper / Author / Year | Problem | Method | Data / tests | Finding | Scope limit
11 | Experimentally Validated Coulomb Counting Method for Battery State-of-Charge Estimation under Variable Current Profiles Zine et al., 2022 | Simple real-time SOC estimation | Current integration | Lead-acid bench tests | Bench SOC workflow | LFP tests still needed
12 | Hybrid State of Charge Estimation of Lithium-Ion Battery Using the Coulomb Counting Method and an Adaptive Unscented Kalman Filter Fahmy et al., 2023 | SOC with changing conditions | Coulomb counting plus adaptive UKF | 2.6 Ah Panasonic simulations | Lower simulated error in comparisons | Numerical results only
13 | State of Charge Estimation of LiFePO4 in Various Temperature Scenarios Wang et al., 2023 | LFP plateau and temperature | Temperature ECM; improved EKF | LFP chamber / load tests | Includes temperature | Needs pack-specific data
14 | Toward Energy Efficient Battery State of Charge Estimation on Embedded Platforms Turkmanović et al., 2024 | Estimator energy versus accuracy | Two EKFs at varied rates | PC accuracy + STM32H7 timing | Sample-rate trade-off | ESP32 timing unknown
15 | Electronic Load for Parameter Characterization in Equivalent Circuit Models of Lithium-Ion Batteries Bampi et al., 2025 | Battery parameter testing | Electronic load + ECM / EKF | LTO cell + ESP32 rig | Parameter and SOC estimates | Different test rig
Notes: These papers inform the proposed project. Findings belong to the cited authors and are not WattSense results. Scope limits describe applicability to the proposed AC signature and DC battery subsystems.
Battery and microgrid studies provide subsystem context. Their particular chemistry, hardware, results and sampling cannot be transferred directly to the proposed household system.
[11] B. Zine, H. Bia, A. Benmouna, M. Becherif, and M. Iqbal, "Experimentally Validated Coulomb Counting Method for Battery State-of-Charge Estimation under Variable Current Profiles," Energies, vol. 15, no. 21, Art. 8172, 2022, doi: 10.3390/en15218172.
https://doi.org/10.3390/en15218172
Evidence: The broad Li-ion discussion in the abstract must not be mistaken for our 4S LFP validation. Initial SOC and suitable measurements are needed; this study is a practical procedure reference.
[12] Hend M. Fahmy, Rania A. Swief, Hany M. Hasanien, Mohammed Alharbi, José Luis Maldonado, and Francisco Jurado, "Hybrid State of Charge Estimation of Lithium-Ion Battery Using the Coulomb Counting Method and an Adaptive Unscented Kalman Filter", Energies, vol. 16, no. 14, Art. 5558, 2023, doi: 10.3390/en16145558.
https://doi.org/10.3390/en16145558
Evidence: The abstract explicitly labels numerical simulations and describes parameter fitting with African Vultures Optimization. The table includes only the estimator core. Do not present this as a physical WattSense comparison.
[13] M. Wang, G. Wang, Z. Xiao, Y. Sun, and Y. Zheng, "State of Charge Estimation of LiFePO4 in Various Temperature Scenarios," Batteries, vol. 9, no. 1, Art. 43, 2023, doi: 10.3390/batteries9010043.
https://doi.org/10.3390/batteries9010043
Evidence: Direct chemistry relevance. Temperature-dependent capacity and the flat OCV region motivate measuring the actual pack instead of relying on the assumed teaching curve. WattSense's fixed-temperature simulation does not reproduce these tests.
[14] H. Turkmanović, I. Popović, and V. Rajović, "Toward Energy Efficient Battery State of Charge Estimation on Embedded Platforms," Electronics, vol. 13, no. 21, Art. 4256, 2024, doi: 10.3390/electronics13214256.
https://doi.org/10.3390/electronics13214256
Evidence: Contrasts Rint and second-order RC EKFs and connects estimator rate to energy cost. Its reported savings cannot be copied to the ESP32; our 0.8 W controller load remains an assumption awaiting measurement.
[15] S. Bampi, G. Waltrich, and A. Vaccari, "Electronic Load for Parameter Characterization in Equivalent Circuit Models of Lithium-Ion Batteries," Eletrônica de Potência, vol. 30, Art. e202521, 2025, doi: 10.18618/REP.e202521.
https://doi.org/10.18618/REP.e202521
Evidence: Publisher full-text reports an ESP32 electronic-load instrument, lithium-titanate cell characterisation and EKF SOC estimation. Useful evidence for a laboratory procedure and embedded integration. Its battery chemistry, electronic-load instrument and estimator differ from the current protected-LFP/INA219 WattSense design; none of its accuracy transfers to our project.
Sources
Current project context: a battery-mounted and battery-powered monitor/adviser. AC appliance signatures support battery demand and runtime guidance. Battery and microgrid papers support sensing, charge estimation and integration. Their results are external evidence, not WattSense measurements.

## Slide 6
6
Literature Survey 4 of 4
No | Research Paper / Author / Year | Problem | Method | Data / tests | Finding | Scope limit
16 | Priority-based low voltage DC microgrid system for rural electrification Marahatta et al., 2021 | Limited rural energy supply | Priority switching + SCADA | Laboratory solar-battery microgrid | Maintains essential-load service | Three-level solar system
17 | Enhanced demand side management for solar-based isolated microgrid system: Load prioritisation and energy optimisation Rajbhandari et al., 2024 | Variable solar supply | Day-ahead forecasts + PSO | Generation / load simulations | Improves priority-load continuity | Requires forecasts and optimisation
18 | Design of a Laboratory Scale Solar Microgrid Cyber-Physical System for Education Guo & Kors, 2021 | Renewable energy teaching | Sensors, Raspberry Pi, SCADA | Outdoor rig + student tests | Integrated educational platform | No signature matching
19 | A standalone DC microgrid energy management strategy using the battery state of charge Yusubov & Bekirova, 2023 | Variable PV output and demand | Power/SOC rules + load shedding | Standalone DC microgrid simulations | Coordinates loads within SOC bounds | No physical validation reported
20 | Energy Management System (EMS) Based on Model Predictive Control (MPC) for an Isolated DC Microgrid Basantes et al., 2023 | Dispatch cost and battery limits | Hierarchical control + MPC | Simulink + FICO Xpress scenarios | Reduces simulated operating cost | Battery degradation model deferred
Notes: These papers inform the proposed project. Findings belong to the cited authors and are not WattSense results. Scope limits describe applicability to the proposed AC signature and DC battery subsystems.
Battery and microgrid studies provide subsystem context. Their particular chemistry, hardware, results and sampling cannot be transferred directly to the proposed household system.
[16] A. Marahatta, Y. Rajbhandari, A. Shrestha, A. Singh, A. Gachhadar, and A. Thapa, 'Priority-based low voltage DC microgrid system for rural electrification,' Energy Reports, vol. 7, pp. 43-51, 2021, doi: 10.1016/j.egyr.2020.11.030.
https://www.sciencedirect.com/science/article/pii/S2352484720314554
Evidence: Publisher explicitly describes experimental analysis and a low-cost SCADA implementation. Saved evidence identifies three load priorities and battery thresholds. This is close prior art, so priority shedding itself is not a new WattSense algorithm. The row states a qualitative study finding and transfers no performance percentage.
[17] Y. Rajbhandari, A. Marahatta, A. Shrestha, A. Gachhadar, A. Thapa, F. Gonzalez-Longatt, and P. Korba, 'Enhanced demand side management for solar-based isolated microgrid system: Load prioritisation and energy optimisation,' IET Smart Grid, vol. 7, no. 3, pp. 294-313, 2024, doi: 10.1049/stg2.12151.
https://ietresearch.onlinelibrary.wiley.com/doi/10.1049/stg2.12151
Evidence: Primary discussion identifies stochastic load/generation simulations, three priority levels and PSO-optimised SOC shedding points using forecasts. Cite issue year 2024 rather than online-first 2023. WattSense has not implemented or evaluated this forecasting/PSO method; the row is external context and transfers no result.
[18] L. Guo and J. Kors, Jr., 'Design of a Laboratory Scale Solar Microgrid Cyber-Physical System for Education,' Electronics, vol. 10, no. 13, Art. 1562, 2021, doi: 10.3390/electronics10131562.
https://www.mdpi.com/2079-9292/10/13/1562
Evidence: Primary paper reports a solar panel, purchased MPPT controller, rechargeable battery, relay-controlled loads and student assessment. Hardware data were sampled every ten minutes in its reported outdoor run. Its focus is educational system integration; it does not establish the proposed WattSense signature estimator or any WattSense measurement.
[19] E. Yusubov and L. Bekirova, 'A standalone DC microgrid energy management strategy using the battery state of charge,' Informatyka, Automatyka, Pomiary w Gospodarce i Ochronie Środowiska, vol. 13, no. 3, pp. 75-78, 2023, doi: 10.35784/iapgos.5320.
https://ph.pollub.pl/index.php/iapgos/en/article/view/5320
Evidence: The publisher abstract explicitly combines available-source power, demand and SOC with load-shedding capability and evaluates an algorithm by simulation. Although authors claim battery-life benefits, the row deliberately uses SOC-limit coordination and does not present lifetime extension as measured cycling data.
[20] J. A. Basantes, D. E. Paredes, J. R. Llanos, D. E. Ortiz, and C. D. Burgos, 'Energy Management System (EMS) Based on Model Predictive Control (MPC) for an Isolated DC Microgrid,' Energies, vol. 16, no. 6, Art. 2912, 2023, doi: 10.3390/en16062912.
https://www.mdpi.com/1996-1073/16/6/2912
Evidence: Metadata/byline was confirmed from the primary published PDF hosted in a research repository. The study compares with/without EMS under radiation and demand disturbances. Its conclusions explicitly defer battery-degradation modeling and diesel-start constraints to future work. Real-time feedback here is within the simulated coupled control system; do not call it real hardware measurement.
Sources
Current project context: a battery-mounted and battery-powered monitor/adviser. AC appliance signatures support battery demand and runtime guidance. Battery and microgrid papers support sensing, charge estimation and integration. Their results are external evidence, not WattSense measurements.

## Slide 7
7
Research Gap / Problem Identification
Proposed contribution: turn battery and load measurements into explainable backup guidance.
Battery percentage alone does not explain usable energy or backup time.
Changing AC/DC loads and inverter losses affect remaining runtime.
Battery-side signatures can overlap or vary with appliance states.
Charging current can hide load demand and needs separate tracking.
Users need advice on optional loads and the expected backup benefit.
Notes: The contribution is battery energy/runtime estimation connected to selected load signatures and actionable, testable guidance. Aggregate battery current does not uniquely identify arbitrary household appliances, especially through an inverter. Begin with known loads/states and controlled recordings, compare trained candidates and reject unknown/ambiguous profiles. Supporting load-side DC sensors or an enclosed isolated AC real-power meter can help separate load demand from net charging current. Charge availability must not be assumed to persist. No universal zero-configuration recognition, physical savings or classifier accuracy has been achieved.
Sources
sih 2026 shubham.pptx
.analysis/review3-signature/literature.json

## Slide 8
8
Problem Statement
Objectives
Develop a battery-mounted device, powered by the battery, that estimates remaining energy and runtime, supports AC/DC loads and solar or AC charging, and recommends which optional loads to turn off.
Measure battery V/I/temperature and supporting load power.
Estimate charge, usable energy and backup with a stated reserve.
Learn 4–6 selected AC/DC load profiles with UNKNOWN handling.
Recommend optional loads to turn off using user-set priorities.
Validate energy/runtime errors and recommendation benefit.
Notes: Use coulomb counting with a valid initial charge reference, independent usable-capacity calibration and chemistry-specific conditions. Voltage alone is not reliable LiFePO4 SOC. Random Forest is a candidate for known-load classification in local Python, compared with a Decision Tree and profile matching. Battery-side signatures must be collected on the actual converter/inverter arrangement; published mains waveforms are not equivalent. Train/tune/test on separate whole sessions. User priorities and estimated load savings drive the recommendation; an uncertain identity must remain UNKNOWN. Present before/after runtime under identical assumptions. Manual advice is the core: no automatic mains relay is claimed.
Sources
sih 2026 shubham.pptx
https://scikit-learn.org/stable/modules/generated/sklearn.ensemble.RandomForestClassifier.html
https://scikit-learn.org/stable/modules/generated/sklearn.model_selection.GroupKFold.html

## Slide 9
9
Proposed System Architecture
Power paths: charging, battery and AC/DC loads
Solar panel
Solar charge
controller
AC mains
Compatible AC/DC
battery charger
Protected
DC system bus
DC/DC
converter
DC loads
Inverter
AC loads
Rated bidirectional
DC current sensor
Battery with
commercial BMS
Regulated
device supply
WattSense
ESP32
Use solar OR AC charging
with compatible equipment
Measurements and processing inside the monitoring system
Battery V/I/temperature
Supporting AC/DC
load measurements
ESP32 + local model
SOC, usable Wh, signatures
Known / UNKNOWN
Display / local dashboard
Energy and backup time
What to turn off and why
Blue connectors: power. Purple connectors: information.
WattSense mounts near the battery. Its demand is included in the monitored power.
Notes: Functional architecture, not mains wiring. POWER: Solar panel -> compatible solar charge controller OR AC mains -> matched isolated AC-to-DC battery charger -> protected DC system bus. Choose one charging path initially; independent chargers may operate together only after documented coordination/backfeed compatibility. Protected battery with commercial BMS <-> appropriately rated bidirectional whole-battery current sensor <-> bus. All battery charging/discharging crosses this sensor; the battery voltage is measured across the appropriate terminals and temperature at the pack, not in series. Bus -> DC/DC converter -> DC loads; bus -> inverter -> AC loads; bus -> qualified regulated supply -> WattSense ESP32. The device sits near the battery and is battery-powered; current coverage includes its own draw. USB data must not backfeed the regulated supply. The power and processing views show the same WattSense device.
SIGNALS: whole-battery V/signed I/temperature, charger or load branch measurements and, where needed, supporting enclosed isolated AC real-power metering feed the ESP32/local model. AC real W/Wh is different from apparent VA; slow metering does not capture raw harmonics/waveforms. A battery terminal sensor alone cannot establish arbitrary per-appliance identities. Calibrated energy/SOC and trained known-load profiles feed remaining Wh/runtime and explainable user recommendations. The user chooses priorities and turns off suggested optional loads manually. No mains switching hardware is claimed.
Existing Rev B INA219 board remains an unbuilt low-power DC foundation with 2 A battery-path and 1.5 A continuous 5 V ceilings. It cannot connect to mains or carry household inverter battery current. Use a separately rated current path/sensor covering the complete battery circuit, not an inverter bypass invisible to the sensor. Battery voltage/chemistry, BMS, charger, controller and inverter compatibility remain to be qualified; never assume a LiFePO4 pack works with a lead-acid UPS charger. Mount monitoring electronics in a suitable enclosure without modifying/sealing battery ventilation or pack protections. This full hardware arrangement and advisory model are proposed, not assembled.
Sources
sih 2026 shubham.pptx
User clarification, 3 October 2026
hardware/PCB_REQUIREMENTS.md
hardware/REFERENCE_WIRING.md
https://www.ti.com/product/INA219

## Slide 10
10
Dataset / Data Collection
Data item | Collection plan
Initial profiles | 4–6 selected AC/DC loads and known operating states
Battery / input data | Time, battery V/I/temperature and charge/load power
Load conditions | One load per run, repeated sessions, mixtures later
Guidance inputs | User priorities, desired backup and estimated load savings
Train / test split | Separate complete sessions for training and final testing
Record battery and load signals on the actual power system.
AC metering follows its verified update rate.
Known-load training and combined AC/DC validation are pending.
Current records demonstrate the DC software foundation.
Notes: Collect measured battery-side profiles with the selected inverter/converters and battery-powered monitor, initially one connected load/state per run. Supporting isolated AC and DC branch meters establish labels, actual power and savings. Record signed battery current, voltage, temperature, timestamps, charging source power and gross load demand where available. Net battery current during charging alone is not gross load demand. Train Random Forest versus Decision Tree and matching baseline on separate complete recording sessions. Save user priorities and desired runtime separately from physical measurements. Calibrate capacity and initial SOC before controlled discharge experiments. No physical dataset or trained model exists. Nominal 10 Hz acquisition and about 1 Hz telemetry apply only to existing DC firmware; no raw AC rate is specified.
Sources
sih 2026 shubham.pptx
firmware/src/main.cpp
https://scikit-learn.org/stable/modules/generated/sklearn.model_selection.GroupKFold.html

## Slide 11
11
Expected Outcomes and Evaluation
Expected output | Evaluation method
Remaining battery energy | Calibrated usable capacity, reference and reserve
Backup-runtime estimate | Prediction error against matched observed discharge
Known / UNKNOWN load | Held-out confusion matrix and unknown acceptance
Turn-off recommendation | Matched before/after demand and backup benefit
AC/DC charging and loads | Check conversion, current coverage and meter error
DC audit (30 Sep): 45 Python tests and 67 C++ assertions.
Both existing ESP32 firmware targets compiled.
Integrated battery-powered guidance and AC/DC performance
require measured validation.
Notes: Existing test counts are historical DC software/CAD foundation evidence, not measured performance of the complete device. Usable Wh needs valid SOC/reference, independently established capacity and the stated normal reserve/cutoff. Runtime approximately usable battery Wh / mean battery-side demand under stated future usage. Measured battery-side load demand includes inverter/controller loss and WattSense self-consumption; do not add those losses again. Default backup assumes no future charging, using gross demand or a battery-only test. Net discharge while solar is active gives only a conditional estimate if charging persists; charging balance must not be presented as infinite guaranteed backup. Recommendation uses optional-load priorities and measured/estimated demand saving, then recomputes before/after runtime with the same reserve and conditions. Ambiguous identity suppresses appliance-specific advice. Measure the benefit rather than promise a saving percentage. Physical integrated performance, trained signatures and recommendation validation remain pending.
Sources
docs/RECHECK_2026-09-30.md
docs/TEST_PLAN.md
sih 2026 shubham.pptx

## Slide 12
12
Project Timeline
Period | Work and milestone
September 2026 | DC firmware, dashboard, PCB design and models
October 2026 | Qualify whole-battery sensing, charging and device supply
November 2026 | Record selected AC/DC profiles and compare classifiers
Dec 2026–Jan 2027 | Validate energy/runtime and turn-off recommendations
Feb–Mar 2027 | Test charging/load cases and complete the final demo
Review 3: 3 October 2026
Final submission: the department’s next-semester schedule
Notes: The clarified core is the battery-mounted, battery-powered monitor/adviser. Qualify complete current sensing and its regulated supply first. Use purchased protected battery equipment and compatible solar controller or AC/DC charger, with no custom BMS. Borrow a compatible battery/inverter system and rated load/reference meters where possible. Current Rev B 2 A path cannot carry household inverter current. Budget below INR 10,000 remains a cap; the old INR 9,700 DC allocation excludes AC integration and does not establish a complete affordable build. Parts, delivery, measured dataset and hardware performance remain pending. Use one charging mode initially, test DC and inverter-fed AC loads under supervised controlled conditions, and leave automatic mains switching/cloud as later optional work. Dates are proposed milestones; final submission follows the department schedule.
Sources
sih 2026 shubham.pptx
User clarification, 3 October 2026
hardware/PCB_REQUIREMENTS.md

## Slide 13
13
References
[1] Athanasiadis et al., 2021
10.3390/en14030767
[2] Mollel et al., 2023
10.3390/s23104845
[3] Jaime et al., 2026
10.3390/inventions11020029
[4] Xiang et al., 2026
10.3390/en19081883
[5] Li et al., 2026
10.3390/en19133131
[6] Movassagh et al., 2021
10.3390/en14144074
[7] Zhang et al., 2018
10.1016/j.energy.2017.10.043
[8] Gismero et al., 2020
10.3390/en13071811
[9] Yang et al., 2021
10.3390/en14041054
[10] Rzepka et al., 2021
10.3390/en14133733
[11] Zine et al., 2022
10.3390/en15218172
[12] Fahmy et al., 2023
10.3390/en16145558
[13] Wang et al., 2023
10.3390/batteries9010043
[14] Turkmanović et al., 2024
10.3390/electronics13214256
[15] Bampi et al., 2025
10.18618/REP.e202521
[16] Marahatta et al., 2021
10.1016/j.egyr.2020.11.030
[17] Rajbhandari et al., 2024
10.1049/stg2.12151
[18] Guo & Kors, 2021
10.3390/electronics10131562
[19] Yusubov & Bekirova, 2023
10.35784/iapgos.5320
[20] Basantes et al., 2023
10.3390/en16062912
Notes: [1] Christos Athanasiadis, Dimitrios Doukas, Theofilos Papadopoulos, Antonios Chrysopoulos, "A Scalable Real-Time Non-Intrusive Load Monitoring System for the Estimation of Household Appliance Power Consumption", Energies, vol. 14, no. 3, Art. 767, 2021, doi: 10.3390/en14030767.
https://www.mdpi.com/1996-1073/14/3/767
Evidence: Primary publisher abstract states three blocks: event detection, CNN classifier and power estimator using active-power turn-on transients. It reports computational/memory efficiency qualitatively. Cached full-page excerpt ends within the introduction, so dataset names, exact sampling rates and numerical performance are not asserted. The limitation cell is an applicability inference: this method needs suitable transient measurements and an already trained target-appliance classifier. It does not validate WattSense, universal detection or zero-configuration deployment.
[2] Rachel Stephen Mollel, Lina Stankovic, Vladimir Stankovic, "Explainability-Informed Feature Selection and Performance Prediction for Nonintrusive Load Monitoring", Sensors, vol. 23, no. 10, Art. 4845, 2023, doi: 10.3390/s23104845.
https://www.mdpi.com/1424-8220/23/10/4845
Evidence: Publisher abstract describes interpretable decision-tree classification, local/global feature importance, REFIT training and unseen same-house/UK-DALE-house evaluation. It reports class-specific improvements, but the displayed row deliberately transfers no percentage to WattSense. Cross-house transfer testing is a design implication drawn from the study setting; the current DC INA219 system cannot inherit its household-data performance.
[3] Herman Cristiano Jaime, Adler Diniz de Souza, Raphael Carlos Santos Machado, Otávio de Souza Martins Gomes, "Machine Learning Models for Non-Intrusive Load Monitoring: A Systematic Review and Meta-Analysis", Inventions, vol. 11, no. 2, Art. 29, 2026, doi: 10.3390/inventions11020029.
https://www.mdpi.com/2411-5134/11/2/29
Evidence: This is a systematic review and meta-analysis, not a new hardware trial. The publisher abstract states 30 eligible studies, random-effects pooling of F1 scores and substantial heterogeneity. Hybrid models had high pooled scores with limited study support; traditional models had broader validation. No pooled score is used as a WattSense result. Issue citation year is 2026; covered primary-study period is 2017-2024.
[4] Haotian Xiang, Wenjing Su, Yi Zong, "Non-Intrusive Load Monitoring: A Systematic Review of Methods, Scenario-Specific Challenges, and Pathways to Practical Deployment", Energies, vol. 19, no. 8, Art. 1883, 2026, doi: 10.3390/en19081883.
https://www.mdpi.com/1996-1073/19/8/1883
Evidence: This is a systematic review/framework, not new hardware validation. Its abstract explicitly identifies real-time/accuracy trade-offs, privacy, unknown loads, behaviour modelling, data quality, transferability, integration and cost. The row is a qualitative synthesis and does not assert a dataset, new classifier or measured accuracy for this review. Relevant to scoping a small known-load prototype with an unknown/ambiguous output.
[5] Yiran Li, Yan Li, Peng Han, "A Non-Intrusive Load Identification Method Based on the Fusion of Steady-State Features and Lightweight Network", Energies, vol. 19, no. 13, Art. 3131, 2026, doi: 10.3390/en19133131.
https://www.mdpi.com/1996-1073/19/13/3131
Evidence: Publisher abstract describes V-I trajectory images plus active/reactive power, trajectory area and slope, fused with a lightweight dual-branch network. Evaluation uses PLAID. The original abstract reports 95.35% recognition accuracy and 0.17M parameters, but these external results are not displayed or attributed to WattSense. This is an AC waveform-based method: the current INA219 DC voltage/current telemetry does not provide synchronised AC V-I trajectories, reactive power or waveform images. The limitation is an explicit sensor/method applicability comparison, not a defect demonstrated by the paper.
[6] K. Movassagh, A. Raihan, B. Balasingam, and K. Pattipati, "A Critical Look at Coulomb Counting Approach for State of Charge Estimation in Batteries," Energies, vol. 14, no. 14, Art. 4074, 2021, doi: 10.3390/en14144074.
https://doi.org/10.3390/en14144074
Evidence: Separates current-measurement, integration, capacity and timing errors. Its results do not establish a WattSense SOC accuracy figure. Calibration/initialization is our design implication.
[7] C. Zhang, W. Allafi, Q. Dinh, P. Ascencio, and J. Marco, "Online estimation of battery equivalent circuit model parameters and state of charge using decoupled least squares technique," Energy, vol. 142, pp. 678–688, 2018, doi: 10.1016/j.energy.2017.10.043.
https://doi.org/10.1016/j.energy.2017.10.043
Evidence: Published in 2018 despite 2017 in DOI. Supports caution about fixed assumed plant parameters. WattSense has not implemented this estimator or measured its pack parameters.
[8] A. Gismero, E. Schaltz, and D.-I. Stroe, "Recursive State of Charge and State of Health Estimation Method for Lithium-Ion Batteries Based on Coulomb Counting and Open Circuit Voltage," Energies, vol. 13, no. 7, Art. 1811, 2020, doi: 10.3390/en13071811.
https://doi.org/10.3390/en13071811
Evidence: Tested aged cells with changing current/temperature. The paper explicitly identifies insufficient relaxation as a capacity-estimation issue. Our LFP pack cannot inherit its NMC OCV map or accuracy.
[9] K. Yang, Y. Tang, and Z. Zhang, "Parameter Identification and State-of-Charge Estimation for Lithium-Ion Batteries Using Separated Time Scales and Extended Kalman Filter," Energies, vol. 14, no. 4, Art. 1054, 2021, doi: 10.3390/en14041054.
https://doi.org/10.3390/en14041054
Evidence: The result is specific to its datasets and estimator. It informs future characterization; WattSense currently uses a simpler current-integration policy, not the published RLS/EKF method.
[10] B. Rzepka, S. Bischof, and T. Blank, "Implementing an Extended Kalman Filter for SoC Estimation of a Li-Ion Battery with Hysteresis: A Step-by-Step Guide," Energies, vol. 14, no. 13, Art. 3733, 2021, doi: 10.3390/en14133733.
https://doi.org/10.3390/en14133733
Evidence: Conclusions compare systematic and rough filter tuning. This is a future-estimator reference, not evidence that WattSense's INA219/current integration achieves the paper's accuracy.
[11] B. Zine, H. Bia, A. Benmouna, M. Becherif, and M. Iqbal, "Experimentally Validated Coulomb Counting Method for Battery State-of-Charge Estimation under Variable Current Profiles," Energies, vol. 15, no. 21, Art. 8172, 2022, doi: 10.3390/en15218172.
https://doi.org/10.3390/en15218172
Evidence: The broad Li-ion discussion in the abstract must not be mistaken for our 4S LFP validation. Initial SOC and suitable measurements are needed; this study is a practical procedure reference.
[12] Hend M. Fahmy, Rania A. Swief, Hany M. Hasanien, Mohammed Alharbi, José Luis Maldonado, and Francisco Jurado, "Hybrid State of Charge Estimation of Lithium-Ion Battery Using the Coulomb Counting Method and an Adaptive Unscented Kalman Filter", Energies, vol. 16, no. 14, Art. 5558, 2023, doi: 10.3390/en16145558.
https://doi.org/10.3390/en16145558
Evidence: The abstract explicitly labels numerical simulations and describes parameter fitting with African Vultures Optimization. The table includes only the estimator core. Do not present this as a physical WattSense comparison.
[13] M. Wang, G. Wang, Z. Xiao, Y. Sun, and Y. Zheng, "State of Charge Estimation of LiFePO4 in Various Temperature Scenarios," Batteries, vol. 9, no. 1, Art. 43, 2023, doi: 10.3390/batteries9010043.
https://doi.org/10.3390/batteries9010043
Evidence: Direct chemistry relevance. Temperature-dependent capacity and the flat OCV region motivate measuring the actual pack instead of relying on the assumed teaching curve. WattSense's fixed-temperature simulation does not reproduce these tests.
[14] H. Turkmanović, I. Popović, and V. Rajović, "Toward Energy Efficient Battery State of Charge Estimation on Embedded Platforms," Electronics, vol. 13, no. 21, Art. 4256, 2024, doi: 10.3390/electronics13214256.
https://doi.org/10.3390/electronics13214256
Evidence: Contrasts Rint and second-order RC EKFs and connects estimator rate to energy cost. Its reported savings cannot be copied to the ESP32; our 0.8 W controller load remains an assumption awaiting measurement.
[15] S. Bampi, G. Waltrich, and A. Vaccari, "Electronic Load for Parameter Characterization in Equivalent Circuit Models of Lithium-Ion Batteries," Eletrônica de Potência, vol. 30, Art. e202521, 2025, doi: 10.18618/REP.e202521.
https://doi.org/10.18618/REP.e202521
Evidence: Publisher full-text reports an ESP32 electronic-load instrument, lithium-titanate cell characterisation and EKF SOC estimation. Useful evidence for a laboratory procedure and embedded integration. Its battery chemistry, electronic-load instrument and estimator differ from the current protected-LFP/INA219 WattSense design; none of its accuracy transfers to our project.
[16] A. Marahatta, Y. Rajbhandari, A. Shrestha, A. Singh, A. Gachhadar, and A. Thapa, 'Priority-based low voltage DC microgrid system for rural electrification,' Energy Reports, vol. 7, pp. 43-51, 2021, doi: 10.1016/j.egyr.2020.11.030.
https://www.sciencedirect.com/science/article/pii/S2352484720314554
Evidence: Publisher explicitly describes experimental analysis and a low-cost SCADA implementation. Saved evidence identifies three load priorities and battery thresholds. This is close prior art, so priority shedding itself is not a new WattSense algorithm. The row states a qualitative study finding and transfers no performance percentage.
[17] Y. Rajbhandari, A. Marahatta, A. Shrestha, A. Gachhadar, A. Thapa, F. Gonzalez-Longatt, and P. Korba, 'Enhanced demand side management for solar-based isolated microgrid system: Load prioritisation and energy optimisation,' IET Smart Grid, vol. 7, no. 3, pp. 294-313, 2024, doi: 10.1049/stg2.12151.
https://ietresearch.onlinelibrary.wiley.com/doi/10.1049/stg2.12151
Evidence: Primary discussion identifies stochastic load/generation simulations, three priority levels and PSO-optimised SOC shedding points using forecasts. Cite issue year 2024 rather than online-first 2023. WattSense has not implemented or evaluated this forecasting/PSO method; the row is external context and transfers no result.
[18] L. Guo and J. Kors, Jr., 'Design of a Laboratory Scale Solar Microgrid Cyber-Physical System for Education,' Electronics, vol. 10, no. 13, Art. 1562, 2021, doi: 10.3390/electronics10131562.
https://www.mdpi.com/2079-9292/10/13/1562
Evidence: Primary paper reports a solar panel, purchased MPPT controller, rechargeable battery, relay-controlled loads and student assessment. Hardware data were sampled every ten minutes in its reported outdoor run. Its focus is educational system integration; it does not establish the proposed WattSense signature estimator or any WattSense measurement.
[19] E. Yusubov and L. Bekirova, 'A standalone DC microgrid energy management strategy using the battery state of charge,' Informatyka, Automatyka, Pomiary w Gospodarce i Ochronie Środowiska, vol. 13, no. 3, pp. 75-78, 2023, doi: 10.35784/iapgos.5320.
https://ph.pollub.pl/index.php/iapgos/en/article/view/5320
Evidence: The publisher abstract explicitly combines available-source power, demand and SOC with load-shedding capability and evaluates an algorithm by simulation. Although authors claim battery-life benefits, the row deliberately uses SOC-limit coordination and does not present lifetime extension as measured cycling data.
[20] J. A. Basantes, D. E. Paredes, J. R. Llanos, D. E. Ortiz, and C. D. Burgos, 'Energy Management System (EMS) Based on Model Predictive Control (MPC) for an Isolated DC Microgrid,' Energies, vol. 16, no. 6, Art. 2912, 2023, doi: 10.3390/en16062912.
https://www.mdpi.com/1996-1073/16/6/2912
Evidence: Metadata/byline was confirmed from the primary published PDF hosted in a research repository. The study compares with/without EMS under radiation and demand disturbances. Its conclusions explicitly defer battery-degradation modeling and diesel-start constraints to future work. Real-time feedback here is within the simulated coupled control system; do not call it real hardware measurement.
Sources

## Slide 14: Thank You Questions and Discussion
14
WattSense
Battery Energy and Runtime Estimation
with Load Signature Guidance
Notes: WattSense is mounted near and powered by the battery. It aims to tell the user remaining usable energy, backup time and which optional load to turn off, using learned signatures and user priorities. Solar or AC/DC charging and DC or inverter-fed AC loads are supported through qualified external equipment. Current prepared items are the DC software/CAD foundation; full hardware integration and measured guidance are pending.
Sources